## HVAC Summary
Date | : 16-05-2025
Project | : DOMBIVALI
Architect | : Livspace
Consultant | : Aeon Airconditioning Solutions
Sl No | Description of Works | Supply Amount in RS | Installation Amount in RS | Total Amount in RS
1 | VARIABLE REFRIGERANT FLOW SYSTEM | 772496.4 | 492425 | 1264921.4
2 | HVAC ELECTRICAL AND CONTROL WORKS | 0 | 105700 | 105700
3 | MISCELLANEOUS ITEMS | 0 | 13000 | 13000
| Grand Total for HVAC Works - Ex Taxes | 772496.4 | 611125 | 1383621.4
| GST 28% | 216298.992 |  | 216298.992
| GST18% | 0 | 110002.5 | 110002.5
| GRAND TOTAL WITH GST |  |  | 1709922.892

## HVAC BOQ
SL.NO | DESCRIPTION | UNIT | GF | 1F | TOTAL QTY | SUPPLY RATE in RS | INSTALLATION RATE in RS | SUPPLY AMOUNT in RS | INSTALLATION AMOUNT | TOTAL
Note: The contractor should read the specifications thoroughly and quote the price for each item. The BOQ should read in conjuction with specification, drawing & equipment schedule. The cost shall include the cost of the material, transportation, taxes, duties, lifting, shifting, storing, handling, installation, testing and commissioning.
I | VARIABLE REFRIGERANT FLOW SYSTEM-
1 | Supply of VRV ODU System
Supply of Variable refrigerant flow(VRF/VRV system for AC System with Fully Inverter Scroll/Fully Inverter Twin/ Single Rotory Compressor technology. The system should be suitable for R 410a/R134a/R32 refrigerant.The Quoted Cost also to include the charges for refrigerant charging.The system should have capacity of loading the compressor capacity from 5%- 100%, based on cooling requirement.The outdoor unit to be with polyester powder coated enclosure,Anticorrosion blue fins for longer life. Noise level should not cross more than 60 dbA at normal operations. The AC System to have its own independent microprocessor controller.The rate should also cover cost for necessary liquid and gas shut off valves and solenoid valves at condensor side. The AC System to have safety devices like high pressure switch fuse,crankcase heater,fusible plug, overload relay, overload protection for inverter, short recycling guard timer.The System to have inbuilt oil recovery system.The quoted rates should also include the costing for canvass connections between ducting and indoor unit also. Quoted AC selected to meet the condition suitable for Mumbai
The configuration of System is as given below.The Quote to be incomplient with specified make and model of equipment. The details of equipment is as given below.The indoor unit to have digital thermostat. The indoor units shall be ceiling mounted ducted type/ Cassette /Hiwall Split Type. The indoor units to have electronic valves to control the refrigerant flow. The fan of the AC Units to be aerodynamically designed and to be balanced statically and dynamically.. The indoor unit to have cleanable type pre filters. Each indoor unit to have computerized PID control for temperature maintaining.Each unit to be with LCD wired remote controller.The indoor unit to be compatible for BMS integration if any. Contractor to quote with specified model of indoor units as below. The indoor unit to have a insulated drain tray .
The configuration of out door and indoor System is as given below.The Quote to be incomplient with specified make and model of equipment. The details of equipment is asgiven below. The product to be Indigenous/Imported. The Compressor technology to be inverted scroll/Inverter Rotory with vapour injection /Inverted rotory technology.Note the VRV system to be BMS compatible it should give Modbus/ Bacnet over LON works
The capacities of Outdoor Units are as below
b | 20HP | Nos |  |  | 0 |  |  | 0 | 0 | 0
c | 16HP | Nos |  |  | 0 |  |  | 0 | 0 | 0
c | 14HP | Nos |  |  | 0 |  |  | 0 | 0 | 0
d | 12HP | Nos |  |  | 0 |  |  | 0 | 0 | 0
e | 10HP- side discharged | Nos | 1 | 1 | 2 | 184184 |  | 368368 | 0 | 368368 | Quoted for Cooling Only model
f | 4HP- side discharged | Nos |  |  | 0 |  |  | 0 | 0 | 0
g | 8HP- side discharged | Nos |  |  | 0 |  |  | 0 | 0 | 0
f | 16HP ODU for TFA hook up with necessary kit | Nos |  |  | 0 |  |  | 0 | 0 | 0
g | 8HP ODU for TFA hook up with neccesary kit | Nos |  |  | 0 |  |  | 0 | 0 | 0
2 | SUPPLY OF INDOOR UNITS FOR VRVs
The indoor units shall be ceiling mounted ducted type/ Cassette/hi wall /TFA type..The Quote to be incomplient with specified make and model of equipment.All below listed indoor units to have electronic valves to control the refrigerant flow. The fan of the AC Units to be aerodynamically designed and to be balanced statically and dynamically.. The indoor unit to have cleanable type filters. Each indoor unit to have computerized PID control for temperature maintaining. scope also covers for suitable coreded/cordless digital thermostat remotes with LCD screen for all the indoor units. The indoor units to be compatible for BMS integration with read /write function for necessary controls through bms.The details of Indoor unit configuration is as given below.With inbuilt drain pump.
2.1 | Supply of Ceiling Suspended type AC : The capacities of Ceiling Suspended type ducted Units(CSU) are as below .The Indoor unit to be with internally insulated preferably with 25mm thick acoustic fibre glass insulation/ suitable cushion or as per OEM. The indoor unit can be direct/ belt driven with two/three speed motor of suitable capacity. The ESP of CSUs s in mm Wg pr ,as mentioned below Utilisation of ACs as per Schedule of Equipment and approval of architects. .Quoted cost includes necessary starters also . Quoted rate also includes suitable prefilter with 20 micron capacity .Drain tray to be insulated with Nitrile rubber insulation.
a | 2.3TR/703cfm ESP as per OEM standards High static | Nos |  |  | 0 |  |  | 0 | 0 | 0
b | 3.2TR/1183cfm ESP as per OEM standards High static | Nos |  |  | 0 |  |  | 0 | 0 | 0
c | 4.6TR/1415cfm ESP as per OEM standards | Nos |  |  | 0 |  |  | 0 | 0 | 0
d | 6.4TR/2400cfm ESP as per OEM standards | Nos |  |  | 0 |  |  | 0 | 0 | 0
e | 8TR/2825cfm ESP as per OEM standards | Nos |  |  | 0 |  |  | 0 | 0 | 0
f | 11TR/4400cfm ESP as per OEM standards | Nos |  |  | 0 |  |  | 0 | 0 | 0
2.2 | Supply of TREATED FRESH AIR UNIT : The capacities of Ceiling Suspended type treated fresh air (TFA) are as below .The Indoor unit to be with internally insulated preferably with 25mm thick acoustic fibre glass insulation/ suitable cushion. The indoor unit can be direct/ belt driven with two/three speed motor of suitable capacity. The ESP of TFAs in mm Wg pr ,as mentioned below Utilisation of TFAs as per Schedule of Equipment and approval of architects. .Quoted cost includes necessary starters also with inbuild drain pump. Quoted rate also includes suitable prefilter with 20 micron capacity .Drain tray to be insulated with Nitrile rubber insulation.
a | 8.0TR/1377cfm ESP as per OEM standards TFA with VRF kit | Nos |  |  | 0 |  |  | 0 | 0 | 0
b | 6.4TR/1024cfm ESP as per OEM standards TFA with VRF kit | Nos |  |  | 0 |  |  | 0 | 0 | 0
2.3 | Supply of 2060cfm Customized Ceiling Suspended DX type TFA : The capacities of Customized DX TFA with 6 or 8 row copper coil for VRV condensor are as below.unit to be constructed with 0.8mm outer and inner sheet of precoated galvanized steel with MERV 8 & MERV 14 filters, the unit to be with internally insulated with 42±3mm thick acoustic PUF insulation OF 48KG/CUM, The Fan should be with plug type fan, TFA. The indoor unit can be direct/ belt driven with three speed motor of suitable capacity. The ESP of TFA to be with 32-40mm ESP of Wg Pr. Utilisation of TFAs as per Schedule of Equipment and approval of architects.Quoted rate also includes suitable plenum box for fresh air & return air , TFA will be connected to 16HP VRV ODU units. TFA will be placed in the balcony Outdoor temp is 43degC inside shall be 14+/- 2 deg C | Nos |  |  | 0 |  |  | 0 | 0 | 0
2.4 | Supply of Cassette AC .The capacities of indoor Units with 4 way ceiling mounted cassette ACs .The Indoor unit to be with cleanable filters. The indoor unit can be direct with three speed motor of suitable capacity. Utilisation of ACs as per DBR and HVAC drawings with approval from architects.Indoor unit to have In-Built Drain pump All Units to have BMS compatibility.
a | 4.0TR -1236cfm -847cfm Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
b | 3.2TR -1024cfm -706cfm Round flow | Nos | 2 | 2 | 4 | 49693.8 |  | 198775.2 | 0 | 198775.2 | Quoted for Rpund flow 4-way cassette with refnets, panel & wireless remotes
c | 2.6TR -812cfm -530cfm- Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
d | 2.0TR -830cfm-530cfm - Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
e | 1.6TR -812cfm-459cfm - Round flow | Nos | 2 |  | 2 | 43295.2 |  | 86590.4 | 0 | 86590.4
f | 1.3TR -533cfm -383cfm- Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
g | 1.0TR -600cfm-459cfm - Round flow | Nos | 1 | 2 | 3 | 39587.6 |  | 118762.8 | 0 | 118762.8
h | 0.8TR -459cfm -353cfm- Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
i | 1.6TR -459cfm-318cfm Compact Multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
j | 1.3TR -388cfm - 265cfm Compact Multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
k | 1.0TR -335cfm-247cfm - Compact Multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
l | 0.8TR -244cfm-140cfm - Compact multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
m | 0.6TR -300cfm-229cfm - Compact multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
Supply of HI WALL Acs-The Indoor unit to be with cleanable filters. The indoor unit can be direct with three speed motor of suitable capacity. Utilisation of ACs as per DBR and HVAC drawings with approval from consultants .
2.5 | The Details of HI WALL AC s.Quoted rate also include Supports for suspending AC units as per Seismic Condition of Building. Scope includes providing plug top with 3 Rmt of multi core cable till AC unit- Scope also includes thermostatic cordless Ac remotes.
b | 1.0 TR -388 cfm | Nos |  |  | 0 |  |  | 0 | 0 | 0
c | 0.8 TR -318cfm | Nos |  |  | 0 |  |  | 0 | 0 | 0
3 | Installation of VRV Units
3.1 | Shifting, Installation, testing and commissioning of VRV Condensor Units. The Quoted rate to include charges towards first charge of oil for indoor/outdoor units, air filter protections. The cost also to include cost for control/power cable terminations with supply and laying of necessary multicore copper cables in PVC/MS conduit from isolator to vrf odu ( Isolator near the odu will be provided by ELE agency).The details of Units are as given below.Scope also covers for lifting of AC Units till allotted space with necessary arrangements(like crane). Quoted Rate also Body Earthing with GI Wire for outdoor unit from Isolator provided by electrical agency.Quoted rated also includes installation of necessary vibration isolators & Cowl piece for outdoor unit as per site condition. Scope also included preesure testing with nitrogen gas & Vaccumising including all consumables.Note Scope includes Pressure testing each circuit with nitrogen Gas, Vaccumising Including all consumables for all floor VRV systems(VRF UNITS) and First Charge of Refrigerant gas
The Quote to be incomplient with installation of a Bacnet protocol for all the VRF units mentioned below for BMS integration with read and write option
The quoted rate also includes cost for crane if needed to lift condenser
The details of VRV is as given below.
a | 20HP | Nos |  |  | 0 |  |  | 0 | 0 | 0
b | 16HP | Nos |  |  | 0 |  |  | 0 | 0 | 0
c | 12HP | Nos |  |  | 0 |  |  | 0 | 0 | 0
d | 10HP- side discharged | Nos | 1 | 1 | 2 |  | 12000 | 0 | 24000 | 24000
e | 4HP- side discharged | Nos |  |  | 0 |  |  | 0 | 0 | 0
f | 16HP ODU for TFA hook up with necessary kit | Nos |  |  | 0 |  |  | 0 | 0 | 0
g | 8HP ODU for TFA hook up with neccesary kit | Nos |  |  | 0 |  |  | 0 | 0 | 0
3.2 | Shifting , assembly , instalation testing and commissioning of Ceiling Suspended type AC : The capacities of Ceiling Suspended type ducted Units(CSU) are as below .The Indoor unit to be with internally insulated with 25mm thick acoustic fibre glass insulation. The indoor unit can be direct/ belt driven with two/three speed motor of suitable capacity. The ESP of CSUs s in mm Wg pr ,as mentioned below Utilisation of ACs as per Schedule of Equipment and approval of architects. .Quoted cost includes necessary starters also . Quoted rate also includes suitable prefilter with 20 micron capacity for CSUs.canvass
a | 2.3TR/703cfm ESP as per OEM standards High static | Nos |  |  | 0 |  |  | 0 | 0 | 0
b | 3.2TR/1183cfm ESP as per OEM standards High static | Nos |  |  | 0 |  |  | 0 | 0 | 0
c | 4.6TR/1415cfm ESP as per OEM standards | Nos |  |  | 0 |  |  | 0 | 0 | 0
d | 6.4TR/2400cfm ESP as per OEM standards | Nos |  |  | 0 |  |  | 0 | 0 | 0
e | 8TR/2825cfm ESP as per OEM standards | Nos |  |  | 0 |  |  | 0 | 0 | 0
f | 11TR/4400cfm ESP as per OEM standards | Nos |  |  | 0 |  |  | 0 | 0 | 0
3.3 | Shifting, Installation, testing and commissioning of of TREATED FRESH AIR UNIT : The capacities of Ceiling Suspended type treated fresh air (TFA) are as below .The Indoor unit to be with internally insulated preferably with 25mm thick acoustic fibre glass insulation/ suitable cushion. The indoor unit can be direct/ belt driven with two/three speed motor of suitable capacity. The ESP of TFAs in mm Wg pr ,as mentioned below Utilisation of TFAs as per Schedule of Equipment and approval of architects. .Quoted cost includes necessary starters also with inbuild drain pump. Quoted rate also includes suitable prefilter with 20 micron capacity .Drain tray to be insulated with Nitrile rubber insulation.
a | 8.0TR/1377cfm ESP as per OEM standards TFA with VRF kit | Nos |  |  | 0 |  |  | 0 | 0 | 0
b | 6.4TR/1024cfm ESP as per OEM standards TFA with VRF kit | Nos |  |  | 0 |  |  | 0 | 0 | 0
3.4 | Shifting , assembly , installation , testing and commissioning of 2060cfm Customized Ceiling Suspended DX type TFA : The capacities of Customized DX TFA with 6 or 8 row copper coil for VRV condensor are as below.unit to be constructed with 0.8mm outer and inner sheet of precoated galvanized steel with MERV 8 & MERV 14 filters, the unit to be with internally insulated with 42±3mm thick acoustic PUF insulation OF 48KG/CUM, The Fan should be with plug type fan, TFA. The indoor unit can be direct/ belt driven with three speed motor of suitable capacity. The ESP of TFA to be with 32-40mm ESP of Wg Pr. Utilisation of TFAs as per Schedule of Equipment and approval of architects.Quoted rate also includes suitable plenum box for fresh air & return air , TFA will be connected to 16HP VRV ODU units. TFA will be placed in the balcony Outddor temp is 43degC inside shall be 14+/- 2 deg C | Nos |  |  | 0 |  |  | 0 | 0 | 0
4 | Shifting, Assembly, Installation, Testing and Commissioning of Cassette ACs The Details of DX ceiling suspended 4 way cassette AC s.Quote rate also include Supports for suspending AC units as per Seismic Condition of Building. Scope includes providing plug top with 3 Rmt of multi core cable till AC unit. Quoted rate also includes power plug top.Note Scope includes Pressure testing each circuit with nitrogen Gas, Vaccumising Including all consumables for all floor VRV systems(VRF UNITS) and First Charge of Refrigerant gas
a | 4.0TR -1236cfm -847cfm Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
b | 3.2TR -1024cfm -706cfm Round flow | Nos | 2 | 2 | 4 |  | 2800 | 0 | 11200 | 11200
c | 2.6TR -812cfm -530cfm- Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
d | 2.0TR -671cfm-530cfm - Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
e | 1.6TR -671cfm-459cfm - Round flow | Nos | 2 |  | 2 |  | 2800 | 0 | 5600 | 5600
f | 1.3TR -533cfm -383cfm- Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
g | 1.0TR -600cfm-459cfm - Round flow | Nos | 1 | 2 | 3 |  | 2800 | 0 | 8400 | 8400
h | 0.8TR -459cfm -353cfm- Round flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
i | 1.6TR -459cfm-318cfm Compact Multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
j | 1.3TR -388cfm - 265cfm Compact Multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
k | 1.0TR -335cfm-247cfm - Compact Multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
l | 0.8TR -244cfm-140cfm - Compact multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
m | 0.6TR -300cfm-229cfm - Compact multi flow | Nos |  |  | 0 |  |  | 0 | 0 | 0
4.1 | Shifting ,Installation testing and commissioning of Hiwall Acs of below capacities. Scope includes providing plug top with 3 Rmt of multi core cable till AC unit
b | 1.0 TR -388 cfm | Nos |  |  | 0 |  |  |  | 0 | 0
c | 0.8 TR -318cfm | Nos |  |  | 0 |  |  |  | 0 | 0
5 | Supply and Fixing of new Refnet Joint complete installation with necessary fixtures will be in standard as per the make of ACs supplied.Contractor t follow the drawing and quote accordingly. Refnet joints to be supplied and installed as per manufacturers recommendations | Set | 4 | 3 | 7 |  | 3500 | 0 | 24500 | 24500
6 | Supply, laying and testing of Hard drawn Refrigerant copper piping of (19 G) For pipes above 12.5mm sizes / 1 mm wall thickness)) & Pipes lesser than 12.5mm with wall thickness of 0.7mm ,between Indoor & Outdoor units.with necessary fittings, controls andsuitable brazed joints. The piping system after completion should be pressure tested for 450-500 PSI of pressure for a period of 24 Hrs and the system to be evacuated to minimum of 28 inch of Hg held for 24 hrs. The piping system should be covered with 13 mm thick Nitrile rubber tube insulation (Quoted rate includes also additional polysheild coating with 2 coats of resin and hardener only for exposed insulation laid externall outside the conditioned space)
a | Dia55.98mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
b | Dia 44.5mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
c | Dia 41.3mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
d | Dia 38.1mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
e | Dia34.9mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
f | Dia31.8mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
g | Dia25.4mm | Rmt | 22 | 24 | 46 |  | 1500 | 0 | 69000 | 69000
h | Dia22.2mm | Rmt | 18 | 10 | 28 |  | 1500 | 0 | 42000 | 42000
i | Dia19.1mm | Rmt | 14 | 10 | 24 |  | 1500 | 0 | 36000 | 36000
j | Dia15.9mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
k | Dia12.7mm | Rmt | 40 | 34 | 74 |  | 1500 | 0 | 111000 | 111000
l | Dia9.53mm | Rmt | 14 | 10 | 24 |  | 1500 | 0 | 36000 | 36000
m | Dia6.24mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
7 | SITC of drain piping complete with PVC, fitting, accessories, bends, elbows, tees, flanges, tappings, wall sleeves, hangers, supports, anchors and insulation using tubular 9 mm nitrile rubber.The piping shall be connected to the nearest drain pipe at site.Do note that AC drain line to be connected to HVAC down take line only and not at any other location. Line to be properly terminated with Y piece / sealed connection. Also pipe to be insulated in shaft if required.
a | Dia 65mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
b | Dia 50mm | Rmt |  |  | 0 |  |  | 0 | 0 | 0
c | Dia 40mm | Rmt | 15 | 10 | 25 |  | 225 | 0 | 5625 | 5625
d | Dia 32mm | Rmt | 10 | 10 | 20 |  | 200 | 0 | 4000 | 4000
e | Dia 25mm | Rmt | 10 | 10 | 20 |  | 175 | 0 | 3500 | 3500
f | Dia 19mm | Rmt |  | 0 | 0 |  |  | 0 | 0 | 0
8 | Supply and Installation of MS angle Steel supports , Scope includes supports for placing the AC Condensors includes VRV Condensor and AC Condensors and also for the supports from the ceiling to suspend ducts and AC units with neccessary anchor fasteners . Scope includes suitable railing and ladder . Suitable 2 coats of primers and a coat of enamel,Supply and Fixing of M.S Stand for Condensing units duly painted by redoxide and 2 rounds of enamel coating of black paint on it. | Kgs | 60 | 60 | 120 |  | 230 | 0 | 27600 | 27600
9 | Supply and laying of 2 mm thick 300x50 perforated powder coated tray without cover in internal building area | Rmt |  |  | 0 |  |  | 0 | 0 | 0
10 | Supply and laying of 2mm thick 300x50 perforated powder coated tray with cover from top in external side of area | Rmt |  |  | 0 |  |  | 0 | 0 | 0
11 | Supply and laying of 1.2 mm thick 150x75 perforated powder coated tray without cover in internal building area | Rmt | 60 | 10 | 70 |  | 1200 | 0 | 84000 | 84000
12 | Supply and laying of 2mm thick 150x75 perforated powder coated tray with cover from top in external side of area | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0
13 | Supply and laying of 9mm thick 24 G GSS drain tray for Hiwall AC | Sqm | 0 | 0 | 0 |  |  | 0 | 0 | 0
14 | Supply and fixing of compact 2L Drain pumps. Pumps to have interlock with units & to have alarm buzzer in case of pump failure. Units to shut off if pump fails. Pump to power socket is part of scope. Cables to be runned in the PVC Conduit. | Nos |  | 0 | 0 |  |  | 0 | 0 | 0
15 | SITC of Twin condensate pump SWAP2-RS manufactured from rigid PVC with (2 + 2) litrestank capacity. The unit should be capable of pumping water to a height of 10m and a with maximum flow rate of 1070L/hour. The unit should run continuouswith Power rating of 0.38A. In case of failure of any single pump with the help of Electronic Control Panel Secondary Pump should auto start with primary pump fail indication by buzzer.The controller should be capable of interchanging the pump on time base and should be capable of BMS connectivity. Pump complete with control panel and copper control cabling in FRLS PVC conduit | Nos |  |  | 0 |  |  | 0 | 0 | 0
16 | Supply and Fixing of Centralized Group controller/ graphic controller (I-Touch Controller) with touch Screen display to give complete control of AC System, able to control the VRV indoor units proposed for the project/ VRV manufactturers recommendations groups of indoor units. It has to switch on/ stop AC Unit, Setting of temperature for indoor units,controlling of fan speed, monitoring of operation status, display of operation history. Timer schedule,Scheduling of outdoor units ,Changeover of Condenser if power fails in one, error report , Generating report for weeky and monthly. The equipment to have Unified On/Off Controller,and scheduled timer for controlling the VRV and ducted split AC Units Includes wiring for centrallised controller also. Note: Controller should be capable of controlling all above Listed VRF ACS with complete cabling | Lot |  |  | 0 |  |  | 0 | 0 | 0
17 | Charges for integration of entire VRV with Fire alarm system with hardwares including neccesry potential free contactors for entire HVAC system | Lot |  |  | 0 |  |  | 0 | 0 | 0
18 | Vibration Isolation Pads (VIP) for VRF/VRV,
| Vibration Isolation Pads (VIP) should be made up of a high quality mixed cellular polyurethane elastomer material of Sylomer Sylodyn.. The material should have excellent vibration isolation characteristics consistently for a very long duration and should reduce structure borne noise, thickness of material shall be as per the OEM recommendation , Load range can be :0.011 N/mm2 to 12 N/mm2 , Temperature range: -30°C to +70°C , ECO-confirmation: Free from VOC, Softening agents, CMR substances, halogenated organic compounds, PVC, NMMO. Chemical resistance: Excellent resistance to water, aqueous solutions, oil, acids, bases, ozone, UV radiation etc.- Scope for VRF Condensor unit only | Set |  |  | 0 |  |  | 0 | 0 | 0
19 | Supply and installation of shutoff valve for the copper pipes | Set |  |  | 0 |  |  | 0 | 0 | 0
20 | Building Mangement system (Integrator) to connect above units complete with all necessary software with open protocol.VRV System vendor to provide output in Open protocol formats, with all units in Daisy Chain Config., on a RS 485 port on master unit. To provide functions for Monitor & Control , Serial Communication of complete VRV Parametres with READ & WRITE facility | Lot |  |  | 0 |  |  | 0 | 0 | 0
| Subtotal of DX VRF AC | [6 empty] | 772496.4 | 492425 | 1264921.4
II | HVAC ELECTRICAL AND CONTROL WORKS
1 | POWER CABLING
Note all copper cables to be FRLS
Supply, laying, affecting connections & Testing of the following sizes of 1.1 KV armoured PVC insulated aluminium/ copper conductor cables. Cables shall be inclusive of all clamps, saddles, screws, cable identification tags, cable terminal joints including terminal lugs, insulating tapes, affecting terminal connections to the equipment as per the specifications and as required.Quoted price shall be inclusive of GI perforated cable trays & supports.
a | 4C x 25 Sqmm cable (Copper) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
b | 4C x 16 Sqmm cable (Copper) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
c | 4C x 10 Sqmm cable (Copper) | Rmt | 40 | 0 | 40 |  | 900 | 0 | 36000 | 36000
d | 4C x 6 Sqmm cable (Copper) | Rmt | 5 | 5 | 10 |  | 550 | 0 | 5500 | 5500
e | 4C x 4 Sqmm cable (Copper) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
f | 4C x 2.5 Sqmm cable (Copper) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
g | 3C x 6 Sqmm cable (Copper) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
h | 3C x 4 Sqmm cable (Copper) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
i | 3C x 2.5 Sqmm cable (Copper) | Rmt | 0 | 0 | 0 |  |  | 0 | 0 | 0
j | 3C x 1.5 Sqmm cable (Copper) VRV indoor power | Rmt | 10 | 8 | 18 |  | 195 | 0 | 3510 | 3510
2 | CONTROL WIRING
Supply, laying, affecting connections & testing of the following sizes of control cables between indoor units and outdoor units. Between Panel and AC Equipments, VRV Units , scope includes Supply and laying of 2 mm thick FRLS PVC Conduit Dia 25mm with necessary support and equipments , cables to be with conduits
a | 2C x1.0 Sqmm copper cable ( Multicore)(VAV looping) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
b | 2C x1.5 Sqmm copper cable ( Multicore)(VRF looping) | Rmt | 80 | 72 | 152 |  | 195 | 0 | 29640 | 29640
c | 3C x1.0 Sqmmcopper cable ( Multicore)(VAV power) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
d | 3C x1.5 Sqmm copper cable ( Multicore) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
e | 3C x1.5 Sqmm copper cable ( Armoured) | Rmt |  |  | 0 |  |  | 0 | 0 | 0
f | 4C x1.0Sqmm copper cable | Rmt |  |  | 0 |  |  | 0 | 0 | 0
3 | Supply and laying of 2 mm thick FRLS PVC Conduit Dia 25mm with necessary support and fixtures | Rmt | 70 | 60 | 130 |  | 85 | 0 | 11050 | 11050
4 | EARTHING
Providing & fixing in position the following bare GI tape/ Cu wire including providing all fixing accessories & effecting proper connections.
a | 40mm x 3mm tape | Rmt |  |  | 0
b | 2 x 12 SWG Cu Wire | Rmt |  |  | 0
c | 2 x 8 SWG Cu Wire | Rmt | 80 | 0 | 80 |  | 250 | 0 | 20000 | 20000
| SUB TOTAL HVAC ELECTRICAL AND CONTROL WORKS | [6 empty] | 0 | 105700 | 105700
III | MISCELLANEOUS ITEMS
1.1 | SITC of Wall mount axial fan with gravity louvers of 200 cfm with all necessary hardwares and cables , fans should be BMS compatible | Nos | 2 |  | 2 |  | 4000 | 0 | 8000 | 8000
1.2 | SITC of Wall mount axial fan with gravity louvers of 300 cfm with all necessary hardwares and cables , fans should be BMS compatible | Nos | 1 |  | 1 |  | 5000 | 0 | 5000 | 5000
| SUB TOTAL HVAC MISCELLANEOUS ITEMS | [6 empty] | 0 | 13000 | 13000
| Grand Total Excluding Taxes towards HVAC Works | [6 empty] | 772496.4 | 611125 | 1383621.4
DESIGN CONSIDERATION FOR COSTING
1 | Design temp- 24+/-1Deg C, for both the floor areas (No Direct RH Control)
2 | Individual VRF ODUs considered for individual floors with necessary fittings, piping, control cabeling etc.
3 | VRF ODUs, copper pipe termination has been considered till the floor level area beside toilets.
4 | Wall mounted axial fans has been considered for toilets and for the pantry counter beside the toilets area.
5 | copper pipe trays considered for both the internal & external exposed areas.
EXCLUSIONs
1 | No critical room/ equipment cooling is considered.
2 | No fresh air ventilation fans considered for the VRF IDUs.
3 | Staircase pressurization, under deck roof insulation is excluded
4 | Painting works
5 | All Civil works
6 | BMS works
7 | PAC works
8 | Any Dismanteling works related to the HVAC
9 | No dedicated AC units has been planned

## HVAC MAKE LIST
List of Approved Makes for HVAC Works
Sl No | Description of Equipment | Make
1 | Prefabricated GSS Ducts | ZECO/VEDHA /SEVENSTAR/DEVDUCT
2 | Sheets for ducting | JINDAL/ SAIL/ TATA
3 | Prefabricated Plenum | AIR MASTER/AIRTECH/ AAGHAM/ VEDHA
4 | Prefabricated Sound Attenuators | AIRTECH/CARRYAIRE/ZECO/VEDHA
5 | Nitrile rubber insulation | ARMAFLEX / KFLEX /ALP AEROFLEX
6 | XLPE thermal insulation-for duct | THERMOBREAK/TROCELLEN
7 | PREFABRICATED MS ACCESS DOORS | SAME AS DUCT
8 | VCDs/BDDs/Neck dampers | COMOS/SYSTEM AIR/AIR MASTER / AIRTECH/ SYNCRO/VEDHA
9 | Actuators | BELIMO/SAUTER/SIEMENS/HONEYWELL
10 | Aluminium grilles/Air outlets | COSMOS/AIRMASTER / CARYAIRE/SYSTEMAIR
11 | Spill Air Boxes | COSMOS/SYSTEM AIR/AIR MASTER /AIRTECH/ SYNCRO/VEDHA
12 | Fire Dampers | COSMOS/AIRMASTER/RUSKINTITUS/GREENHECK/SYSTEM AIR
13 | Flexible Duct | SEVENSTAR/SUPAFLEX/UPTWIGA
14 | Butterfly dampers | COSMOS/SYSTEM AIR/AIRTECH/VEDHA/SYNCHRO
12 | Fibreglass | UP TWIGA/OWENSCORNING
15 | VAVs & VAV Controller | DYNACRAFT WITH KMC /SYNCRO WITH DELTA or BELIMO / JCI/NEPTRONIC/ VEDHA WITH BELIMO
16 | MS Conduit | SUPREME/BHARAT/GUPTA
17 | Control Cables | POLYCAB/KEI/BONTON/HAVELLS
18 | CAT-6 Cables | COMSCOPE/DLINK/ MOLEX/SYTSIMAX
19 | Copper Pipes | MANDEV/MEHTATUBES/TOTALLINE/RAJCO/PTPK
20 | Power Cables | POLYCAB/ KEI/BONTON/HAVELLS
21 | Centrifugal SISW/DIDW/Cabinet/ In-line Fans | KRUGER/OSTBERG/NADI/VTS/DYNAIR/NICOTRA
22 | Air Curtain | EURONICS/MITSUBISHI/ORCHID/ AIRODYNE
23 | Motorized VCD | COSMOS/SYSTEM AIR/AIR MASTER /AIRTECH/ SYNCHRO/VEDHA
24 | Cable Tray | CLASSIC/PROFAB/LUMEN
25 | Customized DX CSUs FOR VRF | ZECO/EDGETECH/VTS
26 | CPVC Drain Pipes | ASHIRWAD/ASTRAL/SUPREME
27 | Sequential Panel | THITTANIX/BLUEVOLT /MAPRO/VKAPOWERMASTER
28 | MS Material | JINDAL/ HISSAR/ TATA
29 | MS pipes | TATA/JINDAL/SAIL
30 | Louver | AIRMASTER / CARYAIRE/SYSTEMAIR
31 | Disc valve | AIRMASTER / CARYAIRE/SYSTEMAIR
32 | Co2 Sensors | GREYSTONE/ OMICRON /PRODUAL/ESENSE/HONEYWELL/
33 | H2 Sensor | AMBETRONICS/MSR /RKI/HONEYWELL
34 | DP Switch | SAUTER/ GREYSTONE /DWYER/BELIMO
35 | Drain Pumps | ASPEN/MICRODAM
36 | Motorized fire damper | AIRTECH/AIRMASTER/SYNCHRO/COSMOS/SYSTEM AIR
37 | Panels | THITTANIX/BLUEVOLT /MAPRO/VKAPOWERMASTER
38 | Cushy mount for VRF | BIG FOOT / STRUT FOOT
39 | Paint | ASIAN/NEROLAC
40 | FRLS PVC Conduit | VIP/NELCO/UNIVERSAL
41 | BTU meter | KAMSTRUP/BASICCONTROLS/SIEMENS
42 | Air Handling unit/ CSUs | ZECO/ EDGETECH/ VTS/ BLUESTAR
43 | Spiral Duct | GP SPIRA/DEVDUCT/SPIRALTUBE/ASAWA
44 | VRVs/VRVs | MITSUBISHI/DAIKIN/TOSHIBA/BLUESTAR
45 | Thermowell | DWYER/KELE/EQUIVALENT
46 | AHU Motors | ABB/SIEMENS/HAVELLS/CROMPTON/VTS
47 | AHU Starter | VVPOWER SYSTEM/ PACE/EXCELLENT/LOHA
48 | VFD | DANFOSS/ABB/SIEMENS/FUIJITSU
49 | DX Ducted AC Units | BLUESTAR/CARRIER/DAIKIN/MITSUBISHI
50 | DX Hiwall AC Units | BLUESTAR/CARRIER/DAIKIN/MITSUBISHI
51 | Auto Airvent | ITAP/ANERGY
52 | Chilled water ACs- Hiwall | TRANSCOLD/MIDEA/BHUTORIA
53 | PHI Sensors | ZECO/HONEYWELL/ULTRAFRESH/MAGNETO
54 | UVGI | PUREAIR / ULTRAPURE / UVHEAL / RGF / ZECO/UV HEAL
55 | AIR PURIFICATION & ALLIED | PUREAIR / ULTRAPURE / UVHEAL / RGF / ZECO
56 | IAQ sensors and monitors | HONEYWELL/KAITERRA
57 | Scubbers | ESPAIR/TRION/RYDAIR
58 | Advanced oxidation plasma | ULTRA PURE